**Construction Duration:**  June 17-September 10 with 2nd & 3rd floor scope of work to be completed simultaneously

* + **Third Floor Of Three Story Wing -**Closed to use by individuals
    - Work is scheduled from 6/27 to 9/10
    - **Duration:** 11 weeks with no access to space by occupants
    - Third floor A/C will be shut down during construction.
    - Asbestos containment will be installed in each space which consists of the following:
      * Line floor and walls with 2 layers of 6 mil plastic
      * Remove and reinstall ceiling tiles to clean off any asbestos containing material (ACM) once new roof is installed
      * Wipe down lights, ceiling grid, ducts, and vacuum space
      * Remove plastic containment
      * Asbestos Air Samples will be taken to clear space for occupant use once construction is complete

* + **Second Floor Of Three Story Wing -** Open to access
    - Will remain open but with no A/C
    - 2nd floor A/C will be shut down during construction
    - Temporary cooling systems will be provided only for the following spaces: 2028, 2034, 2048, 2042 & 2049, 2055
    - No asbestos containment will take place on this floor
    - Asbestos Air Monitoring will be conducted every other day at different locations of the floor to document/ensure that occupants are not at risk to asbestos exposure during construction

* + **Second Floor Of Two Story Wing -** Closed to use by individuals.
    - Work is scheduled from 6/17 to 8/2
    - **Duration:** 8 weeks with no access to space by occupants
    - 2nd floor A/C will be shut down during construction
    - Asbestos containment will be installed in each space which consists of the following:
      * Line floor and walls with 6 mil plastic
      * Remove and reinstall ceiling tiles to clean off any asbestos containing material (ACM) once new roof is installed
      * Wipe down lights, ceiling grid, ducts, and vacuum space
      * Remove plastic containment
      * Asbestos Air Samples will be taken to clear space for occupant use once construction is complete

* + **First Floor of Two Story Wing -** Open to use by individuals
    - Floor will remain open to campus activities during construction period
    - First floor A/C will remain operational during construction except for the following spaces which are on a different/separate system: 1119, 1125, 1129 & 1135. Temporary cooling systems will be provided for rooms 1119, 1125, 1129 & 1135 because they are on a separate system from the rest of the first floor
    - No asbestos containment will take place on this floor
    - Asbestos Air Monitoring will be conducted every other day at different locations of the floor to document/ensure that occupants are not at risk to asbestos exposure during construction

* + **First Floor of Three Story Wing -** Open to use by individuals
    - Floor will remain open to campus activities during construction period
    - First floor A/C will remain operational during construction
    - No asbestos containment will take place on this floor
    - Asbestos Air Monitoring will be conducted every other day at different locations of the floor to document/ensure that occupants are not at risk to asbestos exposure during construction